Risk Assessment - Fire

| Responsible Person (Employer or other person having control of the relevant premises) |  | Nicholas Hands |  |  |
| --- | --- | --- | --- | --- |
| Address of Premises |  | Boundless Outdoors Quantry Lane Bell Heath |  |  |
| Postcode |  | DY99UU |  |  |
| Assessor: |  | Nicholas Hands |  |  |
| Date of Fire Risk Assessment |  | April 2019 |  |  |
| Subsequent Review Dates |  |  |  |  |
| Reviewed by | Nicholas Hands |  | Date | 03/04/2020 |
| Reviewed by | Nicholas Hands |  | Date | 20/01/2021 |
| Reviewed by | Nicholas Hands |  | Date | 31/03/2022 |

General Information

| The Premises |  |
| --- | --- |
| Number of floors in building: (To include basements) | Main building:1 Cottage:1 Campsite:1 Campsite tolets:1 Campsite Showers: 1 |
| Brief details of construction: (Date of construction, brick, timber, purpose built or converted) | Main Building: - 1924, Wooden, cement tiles Campsite: - 1990, Brick based building Campsite toilets: - 2022 prefab over timber frame |
| Primary usage: | Main building: group accommodation, centre office, Main kitchens. Cottage: private holiday let Campsite: private camping groups and DofE school groups. |

| Occupancy Profile |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum number of persons in the most highly occupied compartment to be affected by an uncontrolled fire within 30 minutes, assuming no evacuation. | WEEKDAYS |  |  | WEEKENDS |  |  |  |  |
|  | 0000 to 0400 |  | 78 / 100 | 0000 to 0400 |  |  | 78 / 100 |  |
|  | 0400 to 0800 |  | 78 / 100 | 0400 to 0800 |  |  | 78 / 100 |  |
|  | 0800 to 1200 |  | 78 / 100 | 0800 to 1200 |  |  | 78 / 100 |  |
|  | 1200 to 1600 |  | 78 / 100 | 1200 to 1600 |  |  | 78 / 100 |  |
|  | 1600 to 2000 |  | 78 / 100 | 1600 to 2000 |  |  | 78 / 100 |  |
|  | 2000 to 2400 |  | 78 / 100 | 2000 to 2400 |  |  | 78 / 100 |  |
| Description of Occupants | Mobility Issues |  | Average Mobility |  | x | Vulnerability Issues |  |  |

| Occupants Especially At Risk From Fire |  |
| --- | --- |
| Sleeping occupants (Details of numbers - public/staff) | Main centre + Snug: 78+5 Cottage: 8 Campsite: 40 |
| Disabled occupants (Personal Emergency Evacuation Plans in use when necessary) | Main centre: - Maximum 4 occupants |
| Young persons under the age of 16 | Main centre: 72 Campsite: 36 |

Identified Fire Hazards

And Control Measures

| Electrical Sources Of Ignition |  |  |  |  |
| --- | --- | --- | --- | --- |
| Measures taken to prevent fires of electrical origin. |  |  |  |  |
| Fixed installation periodically inspected and tested? (e.g., every 5 years) |  |  | YES |  |
| Portable appliance testing carried out on a risk assessed basis? |  |  | YES |  |
| Suitable policy in place regarding the use of personal electrical appliances? |  |  | YES |  |
| Suitable limitation and management of trailing leads and adaptors? |  |  | YES |  |
| Identified Hazards | Control Measures |  |  | Risk Rating |
| 1. installations inspection 2 Personal electronics 4. Trailing leads 5. Portable heaters 6. cooking items 7. Electrical installations | a. Fixed installation inspection conducted every 5 years by independent company. |  |  | Low Low Low Low Low |
|  | a. Policy is place for clients to use personal electrical items. b. Limited plugs in buildings c. Limited access to mobile sign and Wi-Fi. Groups less lightly to use items then charge them. d. Groups recommended not to bring electrical items. e. No multi plugs in any rooms. |  |  |  |
|  | a. No multi plugs in rooms. b. All long extension leads to be run around the outside of the room. c. Temporary us of extension leads to be removed after use. a. Fan heater not permitted in any part of the main building. b. Only Oil filled radiators to given out by senior staff and not in not supervised areas c. heaters not to be placed in stores or laundry unsupervised a. no cooking items to be used outside of cooking area b. toasters / grills / toasty makers to only be used in kitchen areas and supervised by adults. - Electrical installation only be conducted by registered trades people - All electrical appliances must be CE marked and fit for purpose |  |  |  |
| Deficiencies: |  | Remedial Action Required: |  |  |

| Smoking |  |  |  |  |
| --- | --- | --- | --- | --- |
| Measures taken to prevent fires as a result of smoking. |  |  |  |  |
| Smoking prohibited in the building? |  |  |  | NO |
| Smoking permitted in appropriate areas? |  |  |  | YES |
| Suitable arrangements for those who wish to smoke? |  |  |  | YES |
| Identified Hazards | Control Measures |  | Risk Rating |  |
| 1. Smoking in buildings | a. No Smoking in or around buildings. b. Smoking area is a standalone building |  | Low |  |
| 2. Smoking areas | a. Butts bit provided in smoking area b. under 18’s to be supervised in smoking area. c. visitors notified of smoking area on arrival d. Sand bucket provided to put butts into |  | Low |  |
| 3. Smoking arrangements | a. No Smoking in centre kit. b. suitable time made available to smokers. c. no smoking on session. |  | Low |  |
| 4. Campsite | a. No smocking in camping area / near tents |  | Low |  |
| Deficiencies: No signage for smoking area |  | Remedial Action Required: Add signage for smoking area |  |  |

| Building construction |  |  |  |
| --- | --- | --- | --- |
| Building made of none combustible materials. |  |  | NO |
| Is there a emergency lighting and detection system in place |  |  | YES |
| Are suitable measures taken to minimise the hazard of ignition and building fabric |  |  | YES |
| Identified Hazards | Control Measures |  | Risk rating |
| Building construction (wood) | a.Where possible self closing doors are in place b. emergency lighting and detection system around the building c. zone building areas to limit spread of fire d. Use slow burn materials when replacing current structure elements of 30min burn time ( i.e 12.5mm plaster board) e. On duty members of staff on site when groups are present f. all groups to take part in fire drill and show they can evacuate the building in under 2 minutes |  | Medium |
| Doors | a.Use slow burn doors where possible with fire strips b. Self-closures on all doors Thumb lock on all lockable doors / door must not be lockable from the inside c. All room door to be closed when room is not in use. |  | Medium |
| Roofing | a.All roof spaces to be sealed off to prevent smoke ingress. b. Suspended ceiling should where possible comply with Euroclass B-s1, d0 c. Where solid ceilings are required 30min plaster board should be used when been replaced. |  | Medium |
| Windows (single glazed) | a.All windows to closed when rooms are not in use b. All windows to locked when the building is vacant c. When replacing windows they should be replaced with upvc pains d. Current bedroom windows can be used as a means of fire escape. (45x45cm) |  | Medium |
| Furniture | a.All furniture to have uk fire rating b. Rooms not to be over crowed with item c. No items to be placed in front of electric heater d. No furniture in front of doors. |  |  |
| Deficiencies: Due to the age of the current building there is greater risk than a brick build. |  | Remedial Action Required: Group awareness need to be increased owing to the significant risk compared to a brick building. Additional fire drills for all groups and duty fire marshals are on duty when on groups are one site. |  |
| General Comments: All major works to be conducted by bio mass engineers. If in doubt turn the boiler off and leave until an engineer is present |  |  |  |

| Arson/Deliberate Ignition |  |  |  |  |
| --- | --- | --- | --- | --- |
| Basic security against arson by outsiders or other persons appears reasonable. |  |  | YES |  |
| Is there the potential for fire load/combustibles in close proximity to the premises available for ignition by outsiders? |  |  | NO |  |
| Identified Hazards | Control Measures |  |  | Risk rating |
| 1. Unsanctioned visitors / temptation around site | a. Lock all buildings and windows when not in use. b. Do not leave any flammables unattended on site. c. Move combustible elements away from buildings. E.g., cardboard box etc. d. External monitored CCTV and alarm fitted e. Main gates to be locked when site is not occupied. f. deter unauthorised entry to the site by limiting site entrances, providing appropriate boundary security and implementing controlled site access; g. thoroughly secure all entry points to the premises, including windows and the roof, but make sure that this does not compromise people’s ability to use the escape routes; h. ensure the outside of the building is well lit; i.do not place rubbish skips adjacent to the building; j.do not site wall-mounted waste bins beneath windows k. secure all storerooms, staff restrooms, areas against intrusion at the end of the working day; l. secure flammable liquids |  |  | Low |
| Deficiencies: |  | Remedial Action Required: |  |  |

| Portable Heaters |  |  |  |  |
| --- | --- | --- | --- | --- |
| Portable heaters are used within the premises. |  |  |  | YES |
| Is the use of the more hazardous type (i.e. radiant bar fires or LPG appliances) avoided? |  |  |  | YES |
| Are suitable measures taken to minimise the hazard of ignition of combustible materials due to these heaters? |  |  |  | YES |
| Identified Hazards | Control Measures |  | Risk rating |  |
| 1. Dry clothing | a. All clothing to be dried in the drying rooms or outside b. Wet towels to left over end of beds. |  | Low |  |
| 2. Fan Heaters | a. Fan heaters only to be used in emergencies and in supervised areas. b. no fan heater to be used in wet areas. c. no fan heaters in bedrooms |  | Low |  |
| 3. Heaters in bed rooms | a. Where possible the use of oil filled radiators to be used in bedrooms b. No items to placed over heaters. c. where possible use oil filled radiators. If Electric radiators are used low capacitor, one’s to be used. |  | Low |  |
| Deficiencies: |  | Remedial Action Required: |  |  |
| General Comments: Only portable fire that are suitable to be used with children to be use in the bedrooms |  |  |  |  |

| Fixed Heating Installations |  |  |  |
| --- | --- | --- | --- |
| Fixed heating installations such as boilers are used within the premises. |  |  | YES |
| Are fixed heating installations subject to regular maintenance? |  |  | YES |
| Are suitable measures taken to minimise the hazard of ignition of combustible materials due to these heaters? |  |  | YES |
| Identified Hazards | Control Measures |  | Risk rating |
| 1. Bio Mass | a. all major works to be completed by Bio Mass engineers b. all heating appliances to be serviced and check every 12 months. c. where suitable replacement with electric heating. d. where suitable to use gas cut off valves and safety systems. |  | Low |
| 2. Access to units | All heating controls apart from thermostats to be behind locked doors. |  | Low |
| 3. pellet storage | Pellets to be stored metal silo Pellets to be blown trough piping to clear lines No combustibles to be stored around pellet silo. |  | Low |
| Deficiencies: |  | Remedial Action Required: |  |
| General Comments: All major works to be conducted by bio mass engineers. If in doubt turn the boiler off and leave until an engineer is present |  |  |  |

| Cooking |  |  |  |
| --- | --- | --- | --- |
| Measures taken to prevent fires as a result of cooking. |  |  |  |
| Filters cleaned or changed and ductwork cleaned regularly? |  |  | YES |
| Suitable extinguishing appliances available? (e.g., Fire blanket, Wet Chemical etc) |  |  | YES |
| Suitable Shut Down Procedures in place? |  |  | YES |
| Identified Hazards | Control Measures |  | Risk rating |
| 1. Cooking | a. Only appointed person can use cooking facilities b. No open chip pans to used onsite c. No under 18 to be left unsupervised whilst cooking d. Cooking in camp areas / bush craft to be supervised at all times by staff. e. Where possible extraction units to be used |  | Low |
| 2. Cooking area | a. Area to be clear of hazards. b. No combustibles it be in the area of heat source c. Floors must be clean and dry to avoid slip hazard |  | Low |
| 3. Appointed person in kitchen | a. Only appointed persons may use the kitchen. b. All people using the kitchen must receive an induction on how to use the equipment. c. Deep frier to be left empty after use |  | Low |
| 4. Campfire cooking / bush craft | a. Under 18’s must be supervised at all time cooking outside. b. Some form of extinguishing the fire must be present. c. All combustibles must be removed form area around fire. d. No flammable liquids to be used in lighting a fire. |  | Low |
| 5. Group Kitchen | a. No cooking appliances to be used in group kitchen |  | Low |
| 6. Electrical items | a. Manager visually inspects the system once a year and is competent to do so. b. System inspected and tested by an electrician every five years. c.Staff trained to check equipment before use and to report any defective plugs, discoloured sockets or damaged cable and equipment. d. Staff know where fuse box is and how to safely switch off electricity in an emergency. e. Plugs, sockets etc suitable for kitchen environment. f. Access to fuse box kept clear. |  |  |
| Deficiencies: |  | Remedial Action Required: |  |
| General Comments: |  |  |  |

| Lightning |  |  |  |
| --- | --- | --- | --- |
| The building has a lightning protection system. |  |  | NO |
| Is the lightning protection system subject to a suitable maintenance regime? |  |  | N/A |
| Identified Hazards | Control Measures |  | Risk rating |
| High ropes course strike | High ropes course is earthed through the ground anchors |  | LOW |
| Deficiencies: None of the builds have any lightning protection systems |  | Remedial Action Required: Look into systems but not wholly suitable as buildings are set low into the ground with higher object in the local area. |  |
| General Comments: The centre is set in open country side. The centre footprint is in a low risk area for lightning strike. On the site there is significantly high objects that are earthed and not attached to any building |  |  |  |

| Dangerous Substances |  |  |  |  |
| --- | --- | --- | --- | --- |
| Dangerous substances are, or could be used or stored, within the premises? (i.e. Substantial quantities of alcohol, white spirits, other flammable liquids or materials) |  |  |  | YES |
| A risk assessment has been carried out as required by the Dangerous Substances and Explosive Atmospheres Regulations 2002? |  |  |  | YES |
| Stored in suitable areas and containers away from potential sources of ignition, to include issues of chemical reactivity and compatibility. |  |  |  | YES |
| Identified Hazards | Control Measures |  | Risk rating |  |
| 1. Storage | a. All flammables to be stored in a locked metal container. b. No reactive chemicals to be stored together. c. Reactive chemical to the stored in suitable containers and only in single units. d. No chemicals to be stored near an ignition source. |  | Low |  |
| 2. Use | a. All chimerical to be used in well vented area preferable outside. b. Any spills to be cleaned up immediately |  | Low |  |
| 3. Access | a. Only appointed people to have access the chemicals cupboard. b. Chemicals to be kept in a locked cupboard |  | Low |  |
| Deficiencies: |  | Remedial Action Required: |  |  |
| General Comments: |  |  |  |  |

| Housekeeping |  |  |  |
| --- | --- | --- | --- |
| Standards of housekeeping. |  |  |  |
| Combustible materials appear to be separated from ignition sources? |  |  | YES |
| Appropriate storage of hazardous materials? |  |  | YES |
| Escape routes kept clear of any combustibles? (Storage /furniture) |  |  | YES |
| Appropriate measures for the safe storage and disposal of waste? |  |  | YES |
| Identified Hazards | Control Measures |  | Risk rating |
| 1. Storage of cleaning products | a. All flammables to be stored in a locked metal container. b. No reactive chemicals to be stored together. c. Reactive chemical to the stored in suitable containers and only in single units. d. No chemicals to be stored near an ignition source. e. Combustibles to stored in safe dry room with not ignition sources. |  | Low |
| 2. Use of cleaning products | a. All chimerical to be used in well vented area b. Any spills to be cleaned up immediately |  | Low |
| 3. Access to cleaning cupboard | a. Only appointed people to have access the chemicals cupboard. b. Chemicals to be kept in a locked cupboard |  | Low |
| 4. Storage of bedding | a. All bedding to be stored in a dry place with no access to ignition source. b. All bedding to be locked in cupboards in buildings to prevent access. c. Bedding only to dried in drying room. d. No portable fan heater it be used in storage areas. e. Dirty laundry to be removed from accommodation asap. |  | Low |
| 5. Storage of rubbish | a. All rubbish to be removed from buildings asap. b. Rubbish to be stored in the supplied bins in buildings. c. Over flowing bits and rubbish over flow to be removed to outside bits asap. d. Large outside bins to have segregated waste. e. Outside bins to be stored away from buildings and emptied each week. f. Chemical and other materials to be disposed of asap at local tip etc. |  | Low |
| 6. Laundry | a. Washing machines and tumble drier to be used only under when members of staff present on site. b. Tumble dryer to be cleaned out before each use. c. No combustibles to be stored in laundry room d. Laundry door to be locked at all times. |  | Low |
| 7. Voids | Voids (including roof voids) should not be used for the storage of combustible material. |  | Low |
| Deficiencies: |  | Remedial Action Required: |  |
| General Comments: Whilst areas are been cleaned access to fires exits must be maintained. |  |  |  |

| Hazards Introduced By Contractors And Building Works |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Fire safety conditions have been imposed on both external contractors and in-house maintenance staff? |  |  |  |  | YES |  |
| Is there satisfactory control over works including use of hot work permits, where appropriate, carried out in the building by external contractors? Give details: |  |  |  |  | YES |  |
| If there are in-house maintenance personnel, are suitable precautions taken during works carried out by them, including use of hot work permits, where appropriate? Give details: |  |  |  |  | N/A |  |
| Identified Hazards |  | Control Measures |  |  |  | Risk rating |
| 1. Hot works |  | Hot works only to be carried out by outside contractors risk assesment by contractor must be conducted Visiting groups must not be present areas where hot works are been conducted. All areas of hot works must be checked by additional staff before area is designated safe before leaving site |  |  |  | Low |
| Deficiencies: |  |  | Remedial Action Required: |  |  |  |
| General Comments: All significant works to be carried out by outside contractors. Before work commences risk assessments must be checked and insurance policies. (see contractors risk assesment) |  |  |  |  |  |  |
| Other Significant Fire Hazards That Warrant Consideration |  |  |  |  |  |  |
| Are there any other fire hazards that warrant consideration within the premises? (This to include any fire hazards from any process; heat producing, spark or friction generating, chemical or other process which has the capacity to ignite, create excessive or rapid heat or generate oxidising or flammable gas) |  |  |  |  | YES |  |
| Identified Hazards | Control Measures |  |  |  |  | Risk rating |
| 1. Boiler rooms | a. All boilers have emergency self cut offs. b. All boilers have no combustibles sored near them. c. Boiler located in brick building |  |  |  |  | Low |
| 2. camp site | a. No cooking in tents b. Campfire to be held away from tents. c. Under 18’s to supervised cooking at all times. d. Gas to be turned off when campsite not in use |  |  |  |  | Low |
| 3. Vehicle fires | a. Fire extinguisher to be kept in buses. b. Fire exits in bus to be kept clear. c. Buses to be stored away from buildings and locked when nit in use. d. Buses only to fuelled off site. e. Extra Fuel to only be carried in metal containers. |  |  |  |  | Low |
| 4. Forest fire | a. Keep density of forest litter to a minimum. b. Campfires only to be held in designated areas. |  |  |  |  | Low |
| 5. Furniture | a. ignitability of upholstered furniture (including composites of cover material and infill) and loose covers: BS 5852;83 b. resistance to ignition of upholstered furniture for non-domestic use: BS 7176;84 c. flammability of fabrics for curtains and drapes (including nets and linings): BS 5867-2;59 d burning behaviour (ignitability and flame spread) of curtains and drapes: BS EN 110181 and BS EN 110282 (flame spread); e. assessment and labelling of textile floor coverings: BS 5287;80 |  |  |  |  | Low |
| 6. display board | a. minimise the size and number of display areas to discrete, separated areas; b. do not put displays down stairways which are part of a designated escape route or where there is only one direction of escape (i.e. dead-end conditions); c. keep displays away from curtains, light fittings and heaters; d. keep displays away from ceiling voids which may lack fire barriers; e. ensure that there are no ignition sources in the vicinity; f. ensure displays do not obstruct escape routes or obscure fire notices, fire alarm call points, firefighting equipment or escape signs. |  |  |  |  | Low |
| Deficiencies: |  |  |  | Remedial Action Required: |  |  |

Arrangements for Evacuation

| Evacuation Strategy |  |
| --- | --- |
| Typical evacuation strategies within the premises are likely to involve one or more of the following arrangements. |  |
| Single Stage Evacuation It is reasonably expected that all relevant persons in the premises are able to (and will) evacuate immediately to a place of total safety. | YES |

| Written copies of Evacuation Procedures are located as follows: |  |  |  |  |
| --- | --- | --- | --- | --- |
| See end document. |  |  |  |  |
| Identified Hazards | Existing Control Measures |  |  | Are there any improvement recommendations |
| Door locks | All door locks have barrels that can be opened to exit the room |  | Low |  |
| Doors | Use appropriate doors where possible with self closures and fire strips |  | Low |  |
| Deficiencies: Bedroom doors |  | Remedial Action Required: Replace all bedroom doors with self closure and slow burn material |  |  |

Provision of Elements of Fire Safety as Secondary Control Measures

| Means Of Escape |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| It is considered that the premises are provided with reasonable means of escape in case of fire. Identify the means of evacuation and attach a plan. |  |  |  | YES |  |
| Adequate design of escape routes? |  |  |  | YES |  |
| Reasonable distances of travel when: |  |  |  |  |  |
| Where there is escape in a single direction? State the distance of 100m maximum travel. |  |  |  | YES |  |
| Where there are alternative means of escape? State the distance of 200m maximum travel. |  |  |  | YES |  |
| Suitable protection of escape routes? (Fire resisting construction) |  |  |  | YES |  |
| Adequate provision of exits? State the capacity of each exit. |  |  |  | YES |  |
| Exits easily and immediately open-able where necessary without the use of a key? |  |  |  | YES |  |
| Escape routes unobstructed? |  |  |  | YES |  |
| It is considered that the premises are provided with reasonable arrangements for means of escape for disabled people? Describe the arrangements below. |  |  |  | YES |  |
| Does the evacuation plan fit with the floor space factors? |  |  |  | YES |  |
| Identify dead end corridors. Are the appropriately covered? |  |  |  | YES |  |
| Identify inner rooms. Are the appropriately covered? |  |  |  | YES |  |
| Identified Hazards | Control Measures |  | Risk rating |  |  |
| Building construction (Timber) | - All groups must do a fire drill when arriving on site - A member of staff is present on duty whilst groups are on site - A mains fire alarm and emergency lighting system are in place through the building - Exit from the building must within 2 min of alarm been activated - Fire extinguishers posited around site - Where fire doors are not present fire zones present to mitigate spread - All locked doors must be exit able from both sides - Where possible fire-resistant materials to be used |  | Medium |  |  |
| Deficiencies: |  | Remedial Action Required: |  |  |  |

| Measures To Limit Fire Spread And Development |  |  |  |  |
| --- | --- | --- | --- | --- |
| It is considered that there is: |  |  |  |  |
| Compartmentation of a reasonable standard. (Fire resisting) Identify compartmentation. |  |  |  | NO |
| Reasonable limitation of linings that may promote fire spread. (Walls and ceilings) |  |  |  | NO |
| As far as can be reasonable ascertained, fire dampers are provided in ducts or vents as necessary to protect critical means of escape routes against passage of fire, smoke and combustion products in the early stages of a fire? |  |  |  | YES |
| Identified Hazards | Control Measures |  | Risk rating |  |
| Timber constructed building | - All groups must do a fire drill when arriving on site - A member of staff is present on duty whilst groups are on site - A mains fire alarm and emergency lighting system is in place through the building - Exit from the building must within 2 min of alarm been activated - Fire extinguishers posited around site - Where fire doors are not present fire zones present to mitigate spread - All locked doors must be exit able from both sides Where possible fire-resistant materials to be used - Self-closures to fitted to doors where appropriate |  | Medium |  |
| Cooking | - Cooking and food prep only to take place in kitchen areas. - No gas appliances onsite - Cooking only to be conducted by over 18’s |  | Low |  |
| Laundry | - Laundry only to be used when centre staff or present - Filter to be cleaned before every use - Washing and drying machines should not be loaded in excess of the manufacturer’s recommendations, Items such as cleaning cloths and mop heads placed in the dryers can spontaneously combust if there is any chemical residue left on them. |  | Low |  |
| Building area | - The buildings is divided into different areas by fire doors and walls and floors. These are partly designed to keep a fire within one area, giving people more time to escape. |  | Medium |  |
| Deficiencies: Slow burn materials |  | Remedial Action Required: Due to the age of the building, it is unfeasible to have slow burn or fire lined building materials. Where possible all fire exits are slow burn. |  |  |
| General Comments: Due to the age of the building, it will be impossible to limit the spread of fire. The buildings are made from wood and over 100yrs old. Where possible exit routes are kept to a minimum. |  |  |  |  |

| Emergency Escape Lighting |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| It is considered that there is a reasonable standard of emergency escape lighting to ensure safe use of escape routes complying to BS5266? |  |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  |  | Are there any improvement recommendations |  |
| Un-lit areas | Correct lighting in all areas. Serviced by Fire safe UK |  |  |  |  |
| Exiting building | Light on all exits inside and out |  |  |  |  |
| Bedroom / hall lighting | Emergency lighting system installed with battery back up |  |  |  |  |
| Deficiencies: |  | Remedial Action Required: |  |  |  |

| Fire Safety Signs And Notices |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| It is considered that there is a reasonable standard of fire safety signs and notices? This to include fire exit, fire resisting door and hazard signage. The signage should comply to Health & Safety (Signs and signals) Regulations BS1996 |  |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  |  | Are there any improvement recommendations |  |
| - Exit locations | The correct signage to be used throughout the site |  | Possible zone maps show alarm areas |  |  |
| - Route signage | Arrow pointing to correct nearest exit point |  |  |  |  |
| - Zone map | Zone map depicting alarm areas and detector / sounder locations |  | Update zone map / recover from fire safe |  |  |
| Deficiencies: |  | Remedial Action Required: |  |  |  |

| Means Of Giving Warning In Case Of Fire |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Reasonable manually operated fire warning system provided? |  |  |  |  | YES |
| If yes give details: (e.g., Break glass call points, fire bell, air horn, klaxon etc) |  |  |  |  |  |
| Automatic fire detection provided? If yes, to what Standard? (e.g., BS 5839 Part 1Grade L1/L2 etc) ...........BS5839....................................................................... |  |  |  |  | YES |
| Throughout Premises |  |  |  |  | YES |
| Part of Premises only |  |  |  |  | NO |
| Extent of automatic fire detection generally appropriate for the occupancy and fire risk? |  |  |  |  | YES |
| Remote transmission of alarm signals to a monitoring station or other? |  |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  |  | Are there any improvement recommendations |  |
| 1.Group notification | A. Mains fire alarm system in place b. Duty member of staff present when groups on site |  |  |  |  |
| 2. Auditable alarm | Sounders through out the building |  |  |  |  |
| - Visual alarm | Visual alarm (flashing light) in bedroom area |  |  |  |  |
| Deficiencies: |  | Remedial Action Required: |  |  |  |
| General Comments: Fire alarm system throughout site. Onsite staff monitor alarms whilst groups are on site. |  |  |  |  |  |

| Manual Fire Extinguishing Appliances |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Reasonable provision of portable fire extinguishers? |  |  |  |  | YES |
| Are all fire extinguishing appliances readily accessible and unobstructed? (i.e. mounted on walls or on appropriate bases) |  |  |  |  | YES |
| Is suitable wall signage provided relevant to extinguisher? |  |  |  |  | YES |
| Are hose reels provided? |  |  |  |  | NO |
| Identified Hazards | Existing Control Measures |  |  | Are there any improvement recommendations |  |
| Fire extinguishers | Chub fire services provide and service all extinguishers on site |  |  |  |  |
| Fire blankets | Blankets in kitchens and snug / cottage |  |  |  |  |
| Electrical kill switches | Switches in Kitchen to kill power to appliances |  |  |  |  |
| Hot tubs | Fire extinguishers to be available in property |  |  |  |  |
| Deficiencies: Fire real by main door |  | Remedial Action Required: Needs to be removed |  |  |  |

Management of Fire Safety

| Procedures And Arrangements |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Fire safety is managed by: |  | Nicholas Hands |  |  |  |  |
| Deputy or assistant: |  | Catherine Fitzgerald |  |  |  |  |
| Are competent person(s) appointed to assist in undertaking the preventative and protective measures (i.e. relevant general fire precautions)? State name and responsible element of fire safety Nicholas Hands........... .....Whole Site / staff / visitors.............................. Catherine Fitzgerald ......Whole site / staff / visitors......................... . |  |  |  |  |  | YES |
| Is there a suitable record of the fire safety arrangements? |  |  |  |  |  | YES |
| Appropriate fire procedures in place? |  |  |  |  |  | YES |
| Are procedures in the event of a fire appropriate and properly documented? |  |  |  |  |  | YES |
| Are there suitable arrangements for summoning the Fire and Rescue Service? |  |  |  |  |  | YES |
| Are there suitable arrangements to meet the F&RS on arrival and provide relevant information, including that relating to hazards to fire fighters? |  |  |  |  |  | YES |
| Is there a plan of the building available indicating basic layout and any areas of significant risk? |  |  |  |  |  | YES |
| Are there suitable arrangements for ensuring that the premises have been evacuated? |  |  |  |  |  | YES |
| Is there a suitable fire assembly point(s)? |  |  |  |  |  | YES |
| Are there adequate procedures for evacuation of any disabled people who are likely to be present? |  |  |  |  |  | YES |
| Persons nominated and trained to assist with evacuation, Including evacuation of disabled people? |  |  |  |  |  | YES |
| Appropriate liaison (if necessary) with Fire and Rescue Service Rescue Service crews visiting for familiarisation visits? |  |  |  |  |  | YES |
| Routine in-house inspections of fire precautions (e.g. in the course of health and safety inspections)? |  |  |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  |  |  | Are there any improvement recommendations |  |
| Failure of equipment | All equipment is checked inline with guidance (weekly, monthly, annually) to ensure it is in correct working order and logged appropriately. |  |  |  |  |  |
| Deficiencies: |  |  | Remedial Action Required: |  |  |  |

| Training and Drills |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Fire safety training is managed by: |  |  | Nicholas Hands |  |  |  |
| Deputy or assistant: |  |  | Catherine Fitzgerald |  |  |  |
| Are all staff given adequate fire safety instruction and training on induction? |  |  |  |  |  | YES |
| Are all staff given adequate periodic ‘refresher’ training at suitable intervals? If yes, at what intervals? |  |  |  |  |  | YES |
| Are all staff with special responsibilities (e.g., fire wardens and staff who assist with disabled people) given additional training? |  |  |  |  |  | YES |
| Does all training for staff provide information, instruction or training on the all the following (If no, indicate which one/s in the deficiencies boxes below): |  |  |  |  |  |  |
| Fire risks in the premises? The general fire precautions in the building? Action in the event of a fire? Action on hearing the fire alarm signal? Method of operation of manual call points? Location and use of fire extinguishers? Means for summoning the fire and rescue service? Identity of persons nominated to assist with evacuation? Identity of persons nominated to use fire extinguishing appliances? |  |  |  |  |  | YES |
| Are fire drills carried out at appropriate intervals and a record of such drills maintained? |  |  |  |  |  | YES |
| Are there sufficient and adequate channels of communication of fire safety information between employer and employee (e.g. Health & Safety meetings, notice boards etc) |  |  |  |  |  | YES |
| When the employees of another employer work in the premises, are they provided with adequate instructions and given appropriate information (e.g. on fire risks and fire safety measures)? |  |  |  |  |  | YES |
| Is there adequate co-operation and co-ordination between different Responsible Persons (Multi-Occupancy) to ensure compliance with the Fire Safety Order? |  |  |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  |  |  | Are there any improvement recommendations |  |
| Human error Unknown fire escape routes Contracts on site | Staff training on appointment, annual refresher training and all overnight staff external training – Fire Marshall Regula fire drills for both clients and staff to familiarise themselves with nearest escape routes. Contractors policy they must follow, follow our Risk Assessments and provide their own for specialist work |  |  |  |  |  |
| Deficiencies: |  | Remedial Action Required: |  |  |  |  |
| General Comments: All visiting clients are given a fire brief upon arrival, all residential groups carry out a fire drill and muster at the fire muster point. This allows everyone to be familiar with the closest fire escape route/doors. |  |  |  |  |  |  |

| Testing and Maintenance |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Testing and Maintenance is managed by: |  |  | Fire Safe UK |  |  |  |
| Deputy or assistant: |  |  | Nicholas Hands |  |  |  |
| Adequate maintenance of workplace? |  |  |  |  |  | YES |
| Weekly testing and periodic servicing of fire detection and alarm system to include ancillary equipment (e.g., door hold open devices, door locks etc) |  |  |  |  |  | YES |
| Monthly and annual testing routines for emergency escape lighting? |  |  |  |  |  | YES |
| Annual maintenance of fire extinguishing appliances? |  |  |  |  |  | YES |
| Periodic inspection of external escape staircases and gangways? |  |  |  |  |  | YES |
| Six monthly inspection and annual testing of rising mains? |  |  |  |  |  | YES |
| Weekly and monthly testing, six monthly inspection and annual testing of fire fighting lifts? |  |  |  |  |  | YES |
| Weekly testing and periodic inspection of sprinkler installations? |  |  |  |  |  | N/A |
| Routine checks of final exit doors and/or security fastenings? |  |  |  |  |  | YES |
| Annual inspection and testing of lightning protection system? |  |  |  |  |  | N/A |
| Other relevant inspections or tests: |  |  |  |  |  |  |
| Identified Hazards | Existing Control Measures |  |  |  | Are there any improvement recommendations |  |
| Clients playing with fire extinguishers Equipment failure | Weekly check to ensure they have not been tampered with. Carry out correct maintenance and routine checks with relevant external services when needed i.e. chubb yearly. |  |  |  |  |  |
| Deficiencies: |  | Remedial Action Required: |  |  |  |  |
| General Comments: All inspections are carried out inline with guidance and recorded in the FireChief Log book held in the manager’s office |  |  |  |  |  |  |

| Recording |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Appropriate records held for: |  |  |  |  |  |
| Fire drills? |  |  |  |  | YES |
| Fire training? |  |  |  |  | YES |
| Fire alarm tests? |  |  |  |  | YES |
| Emergency escape lighting tests? |  |  |  |  | YES |
| Maintenance and testing of other fire precaution systems? |  |  |  |  | YES |
| Location of Records: (Available for inspection by Fire Authority if required) Give Details: The Fire Log Book kept in the managers office. |  |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  |  | Are there any improvement recommendations |  |
| Deficiencies: |  | Remedial Action Required: |  |  |  |
| General Comments: All records are held in the office / and relevant log books and are always available for use / inspection including PAT Testing paper work. |  |  |  |  |  |

| Priority | Meaning |
| --- | --- |
| High | Immediate priority to be actioned within 24 hours to 8 weeks Breaches of legal requirements, which could cause injury and require immediate short-term action. Also includes matters that can be resolved at minimal cost |
| Medium | Medium priority to be actioned within 2-6 months Breaches in legislation that may require medium/long term action to resolve |
| Low | Low priority to be actioned within 6 months-1year Items of non urgent priority or for future consideration |

Deficiencies and recommendations identified earlier within this risk assessment should be copied into the following Remedy Action Plan and appropriate action taken.

For an example, see page 32.

| Significant Findings – Remedy Action Plan |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Action to be Taken | Priority | Target Completion Date | Action by | Date Action Completed |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |